## Overview
MTL Foundation Fieldbus Segment Calculator V2.05
Segment OK: 0 errors, 0 warnings.
|  |  |  | Project Name |  | Sample Project
|  |  |  | Segment Name |  | Segment #001
Host Control System |  |  |  | Date | 2026-07-30 | Name
Type |  |  |  | Comments
Host Current | 0 |  |  | Segment Properties
|  |  |  | Default trunk cable type |  |  | 28
|  |  |  | Default spur cable type |  |  | 28
Fieldbus Power Supply |  |  |  | Max ambient cable temperature |  |  | 25
Type |  |  |  | Default field device current |  |  | 17
Voltage | 28 |  |  | Default spur length |  |  | 30
Max Current | 250 |  |  | Field device minimum voltage |  |  | 9.5
Total Current | FALSE |  |  | Spur short circuit test |  |  | Yes
|  |  |  | Total trunk and spur length |  |  | 0
Length | 0 | 28 |  | Max spur length |  |  | 120
Device Coupler 1
Type
Voltage | 28 |  | Load | Length | Resistance | Tag |  | Voltage
Current | 0
Length | 0 | 28
Device Coupler 2
Type
Voltage | 28 |  | Load | Length | Resistance | Tag |  | Voltage
Current | 0
Length | 0 | 28
Device Coupler 3
Type
Voltage | 28 |  | Load | Length | Resistance | Tag |  | Voltage
Current | 0
Approved | [6 empty] | Date
Lines below here should be hidden; set the 'DebugMode' cell to '0'
MaxLength |  |  | Res Coeff |  | Min coupler input voltage |  |  | Max coupler output voltage |  |  | Trunk-to-spur voltagedrop |  |  | Coupler Impedance |  |  | Isolating Supply
1900 |  |  | 1.0195 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
Note on I19: Selecting “Yes” will force the spur causing the lowest spur voltage segment-wide to go into current limit (short circuit) condition. The total current of the coupler where this device is connected to as well as the power supply current will increase accordingly.
Note on I21: Maximum length is 1900m
Note on I22: The maximum recommended spur length depends on the number of spurs: 1-12 120m 13-14 90m 15-18 60m 19-24 30m 25-32 0m
Print

## Errors
Segment OK: 0 errors, 0 warnings.

## Settings (hidden)
|  | Power Supplies |  |  |  |  | Hosts |  |  | Hubs | [13 empty] | Cables |  |  | Trunk Lengths | Segment Lengths | Hub_FFPS_Matrix - Hub/Power supply compatibility Matrix
Debug | 0 | Name | Volts | Current (mA) | Isolating | Selected Index | Name | Current (mA) | Selected Index | Name | Spurs | With ALM every x spurs | Min Input Voltage | Max Output Voltage | Trunk-to-trunk drop | Trunk-to-Spur drop | Max Current | Spur S/C current; -1 means 'No Spurguard' | Impedance Ohms | Max spur device current | Number of Barrier Modules | Algorithm; 1 = FBB model 9373-FB 2 = FBB model 9373-FB2 3 = Megablock | Indices | Name | Resistance | Indices |  |  | Hubs | Power supplies
|  | Custom | 24 | 500 | FALSE | 4 | Custom | 0 | 1 | None | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 1 | Custom | 44 | 5 |  |  |  | Custom | 0 | - 918x-x1 28V N+1 redundancy | 918x-21 (28V 250mA) | 918x-41 (28V 500mA) | 918x-61 (28V 250mA) | 918x-91 (28V 500mA) | 0 | - 918x-x2 19V N+1 redundancy | 918x-22 (19V 250mA) | 918x-42 (19V 500mA) | 918x-62 (19V 250mA) | 918x-92 (19V 500mA) | 0 | - (Redundant) FISCO | 910x-22 (Redundant Ex ib IIB) | 9121-IS (Ex ib IIC) | 9122-IS (Ex ib IIB) | 0 | - F100 non-redundant series | F101 (21.5V 500mA) | F102 (27.9V 500mA) | F104 (13V 250mA) | 0 | - F800 first gen. redundancy | F8xx (F801 modules) | F8xx-2 (F802 modules) | F801 (21.5V 350mA) | F802 (28V 500mA) | 0 | - Classic series supplies | F6x0A (25V 350mA) | FPS-Series (25V 350mA) | 0 | - Other | 28V 400mA
Short Circuit | S/C Index | [5 empty] | Emerson DeltaV | 24 | [14 empty] | 1 | 2.5mm² - AWG 13 | 13 | 5 |  |  | None | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y
No | 2 | - 918x-x1 28V N+1 redundancy |  |  | FALSE |  | Emerson DeltaV S-series powered | 0 |  | - F300 Megablock series | [12 empty] | 1 | 2.1mm² - AWG 14 | 17 |  |  |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y
Yes |  | 918x-21 (28V 250mA) | 28 | 250 | FALSE |  | Honeywell Series C | 24 |  | F304 | 4 |  | 10.4 | 32 | 0.1 | 1.25 | 3.2 | 56 | 0 | 38 |  | 3 |  | 1.5mm² - AWG 15 | 24 |  |  |  | - F300 Megablock series
|  | 918x-41 (28V 500mA) | 28 | 500 | FALSE |  | Yokogawa Centum VP | 0 |  | F308 | 8 |  | 10.5 | 32 | 0.1 | 1.25 | 4.8 | 56 | 0 | 38 |  | 3 |  | 1.3mm² - AWG 16 | 28 |  |  |  | F304 | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
|  | 918x-61 (28V 250mA) | 28 | 250 | FALSE |  | Yokogawa Stardom | 0 |  | F312 | 12 |  | 10.6 | 32 | 0.1 | 1.25 | 6.5 | 56 | 0 | 38 |  | 3 |  | 1.0mm² - AWG 17 | 36 |  |  |  | F308 | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
|  | 918x-91 (28V 500mA) | 28 | 500 | FALSE |  | ABB System 800xA | 0 | [15 empty] | 0.8mm² - AWG 18 | 44 |  |  |  | F312 | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[5 empty] | FALSE |  | Invensys Infusion | 0 |  | - F300 Ex ic compliant Megablocks | [19 empty] | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y
|  | - 918x-x2 19V N+1 redundancy |  |  | FALSE |  |  |  |  | F304 with F30 | 4 |  | 11 | 15.6 | 0.1 | 1.45 | 8.2 | 56 | 0 | 38 |  | 3 | [6 empty] | - F300 Ex ic compliant Megablocks
|  | 918x-22 (19V 250mA) | 19 | 250 | FALSE |  |  |  |  | F308 with F30 | 8 |  | 11 | 15.6 | 0.1 | 1.45 | 9.8 | 56 | 0 | 38 |  | 3 | [6 empty] | F304 with F30 | Y | [8 empty] | Y | Y | Y | Y
|  | 918x-42 (19V 500mA) | 19 | 500 | FALSE |  |  |  |  | F312 with F30 | 12 |  | 11 | 15.6 | 0.1 | 1.45 | 11.5 | 56 | 0 | 38 |  | 3 | [6 empty] | F308 with F30 | Y | [8 empty] | Y | Y | Y | Y
|  | 918x-62 (19V 250mA) | 19 | 250 | FALSE | [23 empty] | F312 with F30 | Y | [8 empty] | Y | Y | Y | Y
|  | 918x-92 (19V 500mA) | 19 | 500 | FALSE |  |  |  |  | - F200 series Ex i Megablocks | [19 empty] | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y
[5 empty] | FALSE |  |  |  |  | F241 (2 spur) | 2 |  | 9.3 | 32 | 0.1 | 0.3 | 1.4 | 40 | 0 | 29 |  | 3 | [6 empty] | - F200 series Ex i Megablocks
|  | - (Redundant) FISCO |  |  | FALSE |  |  |  |  | F245 (4 spur) | 4 |  | 9.3 | 32 | 0.1 | 0.3 | 1.7 | 40 | 0 | 29 |  | 3 | [6 empty] | F241 (2 spur) | Y | [14 empty] | Y | Y | Y
|  | 910x-22 (Redundant Ex ib IIB) | 12.9 | 245 | TRUE |  |  |  |  | F247 (4 spur, T) | 4 |  | 9.3 | 32 | 0.1 | 0.3 | 1.7 | 40 | 0 | 29 |  | 3 | [6 empty] | F245 (4 spur) | Y | [14 empty] | Y | Y | Y
|  | 9121-IS (Ex ib IIC) | 12.4 | 120 | TRUE |  |  |  |  | F251 (8 spur) | 8 |  | 9.3 | 32 | 0.1 | 0.3 | 2.5 | 40 | 0 | 29 |  | 3 | [6 empty] | F247 (4 spur, T) | Y | [14 empty] | Y | Y | Y
|  | 9122-IS (Ex ib IIB) | 13.1 | 265 | TRUE |  |  |  |  | F253 (8 spur, T) | 8 |  | 9.3 | 32 | 0.1 | 0.3 | 2.5 | 40 | 0 | 29 |  | 3 | [6 empty] | F251 (8 spur) | Y | [14 empty] | Y | Y | Y
[5 empty] | FALSE |  |  |  |  | F259 (10 spur, T) | 10 |  | 9.3 | 32 | 0.1 | 0.3 | 2.9 | 40 | 0 | 29 |  | 3 | [6 empty] | F253 (8 spur, T) | Y | [14 empty] | Y | Y | Y
|  | - F100 non-redundant series |  |  | FALSE |  |  |  |  | F261 (10 spur, switched T) | 10 |  | 9.3 | 32 | 0.1 | 0.3 | 2.9 | 40 | 0 | 29 |  | 3 | [6 empty] | F259 (10 spur, T) | Y | [14 empty] | Y | Y | Y
|  | F101 (21.5V 500mA) | 21.5 | 500 | FALSE |  |  |  |  | F271 (12 spur, T) | 12 |  | 9.3 | 32 | 0.1 | 0.3 | 3.2 | 40 | 0 | 29 |  | 3 | [6 empty] | F261 (10 spur, switched T) | Y | [14 empty] | Y | Y | Y
|  | F102 (27.9V 500mA) | 27.9 | 500 | FALSE | [23 empty] | F271 (12 spur, T) | Y | [14 empty] | Y | Y | Y
|  | F104 (13V 250mA) | 13 | 250 | FALSE |  |  |  |  | - F200-XE Ex em Megablocks | [19 empty] | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y
[5 empty] | FALSE |  |  |  |  | F245-XE (4 spur) | 4 |  | 9.3 | 32 | 0.1 | 0.3 | 1.7 | 40 | 0 | 29 |  | 3 | [6 empty] | - F200-XE Ex em Megablocks
|  | - F800 first gen. redundancy |  |  | FALSE |  |  |  |  | F247-XE (4 spur, T) | 4 |  | 9.3 | 32 | 0.1 | 0.3 | 1.7 | 40 | 0 | 29 |  | 3 | [6 empty] | F245-XE (4 spur) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
|  | F8xx (F801 modules) | 21.5 | 350 | FALSE |  |  |  |  | F251-XE (8 spur) | 8 |  | 9.3 | 32 | 0.1 | 0.3 | 2.5 | 40 | 0 | 29 |  | 3 | [6 empty] | F247-XE (4 spur, T) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
|  | F8xx-2 (F802 modules) | 28 | 500 | FALSE |  |  |  |  | F253-XE (8 spur, T) | 8 |  | 9.3 | 32 | 0.1 | 0.3 | 2.5 | 40 | 0 | 29 |  | 3 | [6 empty] | F251-XE (8 spur) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
|  | F801 (21.5V 350mA) | 21.5 | 350 | FALSE |  |  |  |  | F259-XE (10 spur, T) | 10 |  | 9.3 | 32 | 0.1 | 0.3 | 2.9 | 40 | 0 | 29 |  | 3 | [6 empty] | F253-XE (8 spur, T) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
|  | F802 (28V 500mA) | 28 | 500 | FALSE |  |  |  |  | F271-XE (12 spur, T) | 12 |  | 9.3 | 32 | 0.1 | 0.3 | 3.2 | 40 | 0 | 29 |  | 3 | [6 empty] | F259-XE (10 spur, T) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[5 empty] | FALSE | [23 empty] | F271-XE (12 spur, T) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
|  | - Classic series supplies |  |  | FALSE |  |  |  |  | - Classic Megablocks with SpurGuard | [19 empty] | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y
|  | F6x0A (25V 350mA) | 25 | 350 | FALSE |  |  |  |  | FCS-MB2-SG | 2 |  | 10.1 | 32 | 0.1 | 1.1 | 4 | 60 | 0 | 46 |  | 3 | [6 empty] | - Classic Megablocks with SpurGuard
|  | FPS-Series (25V 350mA) | 25 | 350 | FALSE |  |  |  |  | FCS-MB4-SG(-T) | 4 |  | 10.1 | 32 | 0.1 | 1.1 | 4.1 | 60 | 0 | 46 |  | 3 | [6 empty] | FCS-MB2-SG | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[5 empty] | FALSE |  |  |  |  | FCS-MB8-SG(T) | 8 |  | 10.1 | 32 | 0.1 | 1.1 | 4.3 | 60 | 0 | 46 |  | 3 | [6 empty] | FCS-MB4-SG(-T) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
|  | - Other |  |  | FALSE |  |  |  |  | FCS-MB10-SG(-T) | 10 |  | 10.1 | 32 | 0.1 | 1.1 | 4.4 | 60 | 0 | 46 |  | 3 | [6 empty] | FCS-MB8-SG(T) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
|  | 28V 400mA | 28 | 400 | FALSE | If Host="Emerson S-Series with power", this Index 36 is checked |  |  |  | F118 (10 spur, switched T) | 10 |  | 10.1 | 32 | 0.1 | 1.1 | 4.4 | 60 | 0 | 46 |  | 3 | [6 empty] | FCS-MB10-SG(-T) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[10 empty] | FCS-MB12-SG(T) | 12 |  | 10.1 | 32 | 0.1 | 1.1 | 4.5 | 60 | 0 | 46 |  | 3 | [6 empty] | F118 (10 spur, switched T) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[10 empty] | F215 (12 spur, switched T) | 12 |  | 10.1 | 32 | 0.1 | 1.1 | 4.5 | 60 | 0 | 46 |  | 3 | [6 empty] | FCS-MB12-SG(T) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[29 empty] | F215 (12 spur, switched T) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[10 empty] | - Legacy Megablocks without SpurGuard | [19 empty] | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y
[10 empty] | FCS-MB2 | 2 |  | 9 | 32 | 0.1 | 0 | 4.1 | -1 | 0 | 250 |  | 3 | [6 empty] | - Legacy Megablocks without SpurGuard
[10 empty] | FCS-MB4 | 4 |  | 9 | 32 | 0.1 | 0 | 4.1 | -1 | 0 | 250 |  | 3 | [6 empty] | FCS-MB2 | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y |  |  | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[10 empty] | FCS-MB8 | 8 |  | 9 | 32 | 0.1 | 0 | 4.1 | -1 | 0 | 250 |  | 3 | [6 empty] | FCS-MB4 | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y |  |  | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[10 empty] | FCS-MB10-T | 10 |  | 9 | 32 | 0.1 | 0 | 4.1 | -1 | 0 | 250 |  | 3 | [6 empty] | FCS-MB8 | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y |  |  | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[29 empty] | FCS-MB10-T | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y |  |  | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[10 empty] | - Fieldbus barriers | [19 empty] | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y
[10 empty] | 9371-FB (6 spur) | 6 |  | 16 | 13.4 | 0 | 0 |  | 45 | 88 | 40 | 1 | 2 | [6 empty] | - Fieldbus barriers
[10 empty] | 9373-FB (12 spur) | 12 |  | 16 | 13.4 | 0 | 0 |  | 45 | 88 | 40 | 2 | 2 | [6 empty] | 9371-FB (6 spur) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | N |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[10 empty] | 9374-FB (6 spur) | 6 |  | 16 | 13.4 | 0 | 0 |  | 45 | 88 | 40 | 1 | 2 | [6 empty] | 9373-FB (12 spur) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | N |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[10 empty] | 9387-FB (6 spur) | 6 |  | 16 | 13.4 | 0 | 0 |  | 45 | 88 | 40 | 1 | 2 | [6 empty] | 9374-FB (6 spur) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | N |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[10 empty] | 9388-FB (12 spur) | 12 |  | 16 | 13.4 | 0 | 0 |  | 45 | 88 | 40 | 2 | 2 | [6 empty] | 9387-FB (6 spur) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | N |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[29 empty] | 9388-FB (12 spur) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y | [7 empty] | Y | Y | N |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[10 empty] | - Redundant Fieldbus barriers | [19 empty] | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y
[10 empty] | 9372-FB (5 spur red. w/ ALM) | 6 | 6 | 16 | 13.4 | 0 | 0 |  | 45 | 88 | 40 | 2 | 2 | [6 empty] | - Redundant Fieldbus barriers
[10 empty] | 9375-FB (6 spur red.) | 6 |  | 16 | 13.4 | 0 | 0 |  | 45 | 88 | 40 | 2 | 2 | [6 empty] | 9372-FB (5 spur red. w/ ALM) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y |  |  | Y | Y | N |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[10 empty] | 9391-FB (10 spur red. w/ ALM) | 12 | 6 | 16 | 13.4 | 0 | 0 |  | 45 | 88 | 40 | 4 | 2 | [6 empty] | 9375-FB (6 spur red.) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y |  |  | Y | Y | N |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y
[29 empty] | 9391-FB (10 spur red. w/ ALM) | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | Y |  |  | Y | Y | Y |  |  | Y | Y | N |  |  | Y | Y | Y | Y |  |  | Y | Y |  |  | Y

## Calculations (hidden)
Lengths
| Trunk1 | 0 | Coupler1 | 0 | Trunks | 0
| Trunk2 | 0 | Coupler2 | 0 | Spurs | 0
| Trunk3 | 0 | Coupler3 | 0 | Total | 0
|  |  | Currents | Device Current | Voltage ok | Active spur count | Max spur length
|  |  | Coupler1 | 0 | 1 | 0
|  |  | Coupler2 | 0 | 1 | 0
|  |  | Coupler3 | 0 | 1 | 0
Coupler4
0
|  | Spurs | 0 | 13 | 15 | 19 | 25
|  | Max Lengths | 120 | 90 | 60 | 30 | 1
Cells outlined in orange are named

## ReleaseNotes (hidden)
Revision | Date | Comments
2.05 | 2014-12-04 | - Some spur tag name cells were locked, so that tag names could not be changed.
2.04 | 2014-09-23 | - Spur with short circuit simulation will show regular voltage (instead of voltage at current limit)
2.03 | 2014-09-11 | - Minor bug fixes - New Short Circuit spur simulation; now the spur that causes the lowest spur voltage will be chosen. - Added "Print" button
2.02 | 2014-09-05 | - Renamed all FFPS and Megablocks - Minor bug fixes - Added Hub/FFPS-compatibility matrix - Removed "Correct Warnings" button - Automatic check of warnings whenever data is modified
2.01 | 2014-08-20 | Initial Release, based on 937x-FB calculator V2.00. New functions: supports all Megablocks, FBB and FFPS.